## Sheet1
SL. No. | SH | CE’s Sch. Page No. | Item No. | Description of Items | Quantity | Rate | Amount
1 | 1 | 1 | 1.1.1 (i) | Surface channel wiring for the following point looping at the switch board with earth terminal with 1C-2x1.5 sqmm PVC insulated and sheathed stranded cable (BYM) and same size PVC insulated ECC(BYA) (Green / White Color) including circuit wiring with 1C-2x2.5 sqmm PVC insulated and sheathed stranded cable (BYM) & same size PVC insulated ECC(BYA) Green / White color through minimum 1 mm thick PVC channel complete with 18 SWG GP sheet / PVC switch board (preferably concealed) with 3mm thick ebonite sheet cover, circular box, without switch, fixing materials, other accessories etc. as required and mending the damages good. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) and cables shall be manufactured and tested according to relevant IEC / BDS / BS / VDE standards and as per detailed specification mentioned in Annexure-1. The work shall be carried out as per direction & approval of the Engineer. | 12 | 814 | 9768
2 | 6 | 97 | 4.8.1.(iii) | "Supply and fixing bus bar trunking system (800 A and above) both feeder and plugging having the following specification:- * Rated operation voltage 1000V 3-phase, 5 wire. * All bus-bar trunking products and fixing ( straight length, elbow, tees, flanged ends, cable tap box and circuit breaker etc.) shall be in accordance with IEC61439 ; 2012 or UL 857 and from the same manufacturer as per bus bar trunking system. * Short circuit rating: 800 A - 1000 A (40-60 KA/sec) 2500 A - 4000 A (165 -220 KA/sec) * Housing: Constructed of code gauge steel and aluminum to reduce hysteresis and eddy current losses. It shall be totally enclosed non ventilated and anticorrosive ability. * Bus bar: Hard drawn silver plated high conductivity copper of 99.9 % purity. Bus-bar insulation: class B or class F rated polyester film. (No epoxy insulation). * Joint: Bus bar trunking joint shall be of the one-bolt type and shall be possible to remove any joint connection assembly to allow electrical isolation of bus bar trunking length. * Indoor feeder and plug-in trunking shall be hanged 3 meters horizontally and 4.88 meters vertically spacing. * Line to line voltage drop shall not exceed 4% at full connected load. * Temperature rise at any point of the bus bar trunking enclosure shall no exceed 550C." | 10 | 126927 | 1269270
1279038